UAE Commercial Energy Audit Playbook

ASHRAE Standard 211 Level 2 Campaign: 200 Buildings, 60 Days

Dubai, Sharjah and Ajman

Technical and operational framework for audit teams and report compilation

Issue: October 2026

# Contents

# 0. How to Use This Playbook

This playbook directs a 60-day, 200-building ASHRAE Standard 211 Level 2 audit campaign across Dubai, Sharjah and Ajman. It is written for team leads, field auditors, analysts and the report QA reviewer. Each section ends with checklists that can be lifted straight into team briefings.

## 0.1 Campaign arithmetic

| Parameter | Value | Basis |
| --- | --- | --- |
| Buildings | 200 | Contract scope |
| Calendar days | 60 | Contract scope |
| Working field days | ~44 | 6-day week, minus 2 mobilisation days, 4 buffer days, public holidays |
| Site-visits required | 200 walkthroughs + ~60 revisits (logger retrieval, plant rooms) | Revisit rate ~30% |
| Throughput needed | 4.5 to 5 buildings/day campaign-wide | 200 / 44 |
| Field teams | 5 teams of 2 (lead auditor + technician) | 1 building/team/day for large sites, 2/day for small offices/schools |
| Analysis desk | 4 analysts + 1 QA/Technical Director | Reports run 7 to 10 days behind field visits |
| Report output | ~25 to 30 reports per week from week 3 | Pipeline must start in week 2 |

## 0.2 Phasing

| Phase | Days | Key outputs |
| --- | --- | --- |
| P0 Mobilise | 1 to 5 | Rental contracts signed, kits calibrated and tagged, templates locked, utility data requests sent for all 200 buildings |
| P1 Pre-site desk review | 3 to 50 (rolling) | Utility bills loaded, preliminary EUI, building triaged into size/type bands, site-visit pack issued |
| P2 Field survey | 6 to 52 | Walkthrough, spot measurements, logger deployment (7 to 14 days), photo log |
| P3 Analysis & calibration | 10 to 56 | End-use model reconciled within tolerance, EEM list costed |
| P4 Reporting & QA | 14 to 60 | Level 2 report, client review, final issue |

Critical path: utility data. Send DEWA/SEWA/district cooling data requests and owner Letters of Authorisation on day 1. Buildings with no bills by day 20 must be moved to the end of the field schedule.

# 1. Minimum Instrumentation & Field Deployment

## 1.1 Team structure and kit concept

Use three kit tiers so that expensive instruments are pooled rather than duplicated:

- Tier A, Team Kit (x5, one per team): handheld instruments every team uses in every building.

- Tier B, Pooled Specialist Kit (x2): power quality analysers, ultrasonic flow meters, flue gas analyser, high-resolution thermal camera. Booked through a daily kit calendar.

- Tier C, Logger Pool (shared): current/power loggers, temperature/RH loggers, lighting on/off loggers left in buildings for 7 to 14 days.

## 1.2 Tier A: Team kit (per team)

| Category | Instrument | Min. specification | Qty/team | Use |
| --- | --- | --- | --- | --- |
| Electrical | True-RMS clamp meter with power | CAT III 1000 V / CAT IV 600 V, 1000 A AC, kW/PF readout, IEC 61010 | 1 | Spot current, kW, PF on DBs, AHUs, pumps |
| Electrical | Flexible Rogowski clamp | 3000 A, 18 to 24 in. coil | 1 | Large busbars/MDB feeders |
| Electrical | Non-contact voltage tester + insulated gloves | Class 0 gloves | 1 set | Safety |
| HVAC/air | Vane anemometer | 100 mm vane, 0.3 to 30 m/s, +/-2% | 1 | Grille/diffuser velocity, FCU checks |
| HVAC/air | Hot-wire anemometer | 0 to 20 m/s, telescopic probe | 1 | Duct traverse (low velocity) |
| HVAC/air | Thermo-hygrometer | +/-0.3 C, +/-2% RH | 1 | Space, supply, return air |
| HVAC/air | CO2/IAQ meter | NDIR 0 to 5000 ppm | 1 | Ventilation adequacy, DCV opportunity |
| HVAC/air | Digital manometer | +/-0.5% FS, 0 to 2500 Pa | 1 | Filter dP, duct static, Pitot traverse |
| Lighting | Lux meter | Class B (DIN 5032-7), cosine corrected | 1 | Illuminance vs CIBSE/EN 12464-1 |
| Thermal | Thermal camera (entry/mid) | >=160x120, NETD <=60 mK | 1 | Envelope, panels, steam traps, chilled water insulation |
| Thermal | IR thermometer | Adjustable emissivity, 12:1 D:S | 1 | Pipe/surface temperatures |
| Thermal | Contact thermometer (K-type, 2-channel) | +/-0.5 C | 1 | CHW supply/return delta T |
| Spatial | Laser distance meter | 0.05 to 100 m, +/-1.5 mm, area mode | 1 | Floor areas, room volumes |
| General | Tablet with audit app + camera | Offline forms, GPS stamping | 1 | Data capture |
| General | Tachometer (optical/contact) | 0 to 99,999 rpm | 1 | Fan/motor speed |
| Safety | PPE, lock-out tags, torch, ladder (step) | Per site HSE rules | 1 set | Mandatory |

## 1.3 Tier B: Pooled specialist kit (2 sets for 5 teams)

| Instrument | Min. specification | Qty | Use |
| --- | --- | --- | --- |
| 3-phase power quality analyser | IEC 61000-4-30 Class A or S, 4 flex CTs, harmonics to 50th, logging | 3 | MDB/SMDB load profile, chiller kW, harmonics |
| Ultrasonic clamp-on flow meter | Transit-time, DN15 to DN1000, +/-1 to 2% of reading, with thermal energy (BTU) option | 2 | CHW/condenser water flow, pump efficiency, chiller kW/TR |
| Flue gas/combustion analyser | O2, CO, CO2 calc, NOx optional, stack temperature | 1 | Boilers, water heaters, kitchen burners |
| High-resolution thermal camera | >=320x240, NETD <=40 mK, interchangeable lens | 1 | Facades, roofs, MV/LV switchgear |
| Pitot tube set + data-logging manometer | L-type Pitot, ASHRAE 111 traverse | 1 | AHU airflow |
| Balometer (flow hood) | 40 to 4000 m3/h | 1 | Diffuser airflow, fresh air verification |

## 1.4 Tier C: Logger pool

| Logger | Spec | Pool size | Deployment |
| --- | --- | --- | --- |
| Single/3-phase power logger with CTs | 1-min interval, 30-day memory | 25 | 2 to 4 per large building for 7 days |
| Motor on/off & current logger | CT-based | 40 | AHUs, pumps, exhaust fans |
| Lighting on/off/occupancy logger | Light-sensing + PIR | 60 | 4 to 8 per building |
| Temperature/RH logger | +/-0.3 C, 5-min interval | 60 | Zones, CHW pipes |

With 7-day deployments and ~5 sites/day, about 35 buildings are logging at any time; size the pool to 1.5x that demand to cover losses and late retrieval.

## 1.5 Daily field routine (per team)

- 07:00 kit check, battery and calibration-tag check, daily safety brief.

- 08:00 arrival, permit-to-work, FM interview (operating hours, set points, complaints, BMS access).

- 08:45 MDB/SMDB measurements and logger installation (with FM electrician present).

- 09:30 plant room: chillers/CHW ETS, pumps, cooling towers, boilers, water heaters.

- 11:00 AHU/FCU sample survey (minimum 10% of AHUs, 5% of FCUs, all fresh-air units).

- 12:30 lighting and plug-load survey by space type (sample every floor type).

- 13:30 envelope and roof thermography (late morning to afternoon gives best solar-load contrast).

- 14:30 close-out with FM, schedule logger retrieval; upload data the same evening.

## 1.6 Buy versus rent strategy

| Item | Strategy | Rationale |
| --- | --- | --- |
| Clamp meters, lux meters, thermo-hygrometers, IR thermometers, laser meters, vane/hot-wire anemometers, CO2 meters, manometers, tachometers | BUY (x5 to 6 each) | Low unit cost, used daily, kept for future projects; 60-day rental often costs 40 to 70% of purchase price |
| Entry thermal cameras | BUY or long-term rent | Buy if the firm will run further audits within 12 months |
| Power quality analysers | RENT | High capex, calibration-sensitive, only needed at MDB level |
| Ultrasonic flow meters | RENT | High capex, specialist transducers |
| Flue gas analyser | RENT | Few UAE commercial buildings have combustion plant; sensors need recent calibration |
| High-res thermal camera, balometer | RENT | Intermittent use |
| Data loggers | BUY (bulk) | Cheap per unit, high loss risk makes rental damage fees unattractive |

Budget guide: price lists vary by supplier and brand; obtain at least three written quotes. As a rule of thumb, rent anything whose 60-day rental is more than ~60% of its purchase price only if you have no use for it after the campaign.

# 2. Data Reconciliation & Baseline Methodology

## 2.1 Utility data collection

| Provider | Emirate/service | What to request | Notes |
| --- | --- | --- | --- |
| DEWA | Dubai electricity & water | 36 months of bills per account, smart-meter interval data (15/30-min) via owner portal | Owner/tenant consent needed; multi-tenant buildings have many accounts |
| SEWA | Sharjah electricity, water & gas | 24 to 36 months of bills | SEWA also supplies piped gas in parts of Sharjah |
| FEWA / EtihadWE | Ajman and Northern Emirates electricity & water | 24 to 36 months | Ajman is served by Etihad Water & Electricity (formerly FEWA) |
| TAQA / ADDC / AADC | Abu Dhabi | Only if portfolio extends to Abu Dhabi | Out of current scope |
| Empower, Tabreed, Emicool, others | District cooling | Monthly consumption (TRh or RTh), capacity charge (TR contracted), demand, bills | Get the ETS meter readings, not only invoices |
| Gas suppliers (e.g. Emirates Gas, SEWA Gas, Lootah) | LPG/piped gas | Delivery notes or metered consumption | Kitchens, hot water |
| Diesel | Gensets | Fuel purchase log | Usually minor |

## 2.2 Step-by-step reconciliation ("marrying" field data with bills)

- Normalise billing periods. Convert bill periods to calendar months by pro-rating daily: E_month = Σ (E_bill x days_in_month_overlap / days_in_bill).

- Clean the series. Flag estimated reads, meter changes, credit notes, vacancy periods. Remove or annotate outliers (>2 standard deviations from the regression line).

- Weather-normalise. Regress monthly kWh (and TRh) against Cooling Degree Days (base 18 C or 21 C; Dubai/Sharjah stations from Meteostat or degreedays.net). E = a x days + b x CDD. Accept the model if R2 >= 0.75 and CV(RMSE) <= 15% monthly (ASHRAE Guideline 14).

- Separate base load and weather load. The intercept (a) is non-cooling base load (lighting, plugs, lifts, base HVAC fans); the slope term is cooling-dependent load.

- Build the bottom-up inventory from field data (Section 2.3).

- Compare the annual bottom-up total with the normalised annual utility total.

- Calibrate iteratively until annual error is within +/-5% (target) or +/-10% (acceptable), and monthly profile error is within +/-15%.

- Document every adjustment in a calibration log for QA.

## 2.3 Bottom-up end-use model

Each end use is estimated as connected load x load factor x operating hours. Use measured data wherever loggers exist, and spot readings or nameplate data otherwise.

| End use | Formula | Primary data source | Typical share in UAE office |
| --- | --- | --- | --- |
| Cooling (electric chillers/DX) | kWh = Σ(TR_avg x kW/TR x hours) or logged chiller kW | Power analyser on chiller feeders, BMS trend | 45 to 65% |
| Cooling (district) | TRh from ETS meter; convert for EUI (2.5) | DC bills | Replaces chiller electricity |
| Air distribution (AHU/FCU fans) | kWh = Σ(kW_measured x hours x VFD factor) | Clamp spot + run-time loggers | 8 to 15% |
| Pumps (CHW, condenser, booster) | kWh = kW x hours x load factor | Clamp spot + loggers | 3 to 8% |
| Lighting | kWh = Σ(W/m2 x area x hours x usage factor)/1000 | Fixture count, lux, on/off loggers | 10 to 20% |
| Plug/process loads | kWh = Σ(W/m2 x area x EFLH)/1000 | Sample DB metering, inventory | 10 to 20% |
| Domestic hot water | kWh = m x cp x dT / eta | Heater nameplate, occupancy | 1 to 5% (hotels 5 to 10%) |
| Vertical transport | kWh = lifts x kWh/trip x trips | Lift data, ISO 25745 | 2 to 5% |
| Kitchen, data centre, other | Measured/sub-metered | Sub-meters, loggers | Varies |

### Calibration levers (adjust in this order)

- Operating hours and schedules (most uncertain; verify with loggers and BMS).

- Load/diversity factors for plug loads and fans.

- Chiller efficiency at part load (kW/TR curves from logs).

- Unmetered or forgotten loads (car-park ventilation, façade lighting, signage, kitchen exhaust, tenant server rooms).

- Never adjust measured values to force a match; investigate instead.

### Calibration metrics

Annual error (%) = (Model_annual - Utility_annual) / Utility_annual x 100        target |e| <= 5%, max 10%

NMBE (%) = Σ(M_i - S_i) / (n x M_mean) x 100        ASHRAE G14 monthly: within +/-5%

CV(RMSE) (%) = sqrt(Σ(M_i - S_i)^2 / (n - 1)) / M_mean x 100        ASHRAE G14 monthly: <= 15%

## 2.4 Key performance metrics

EUI (kWh/m2/yr) = Σ annual site energy, all fuels converted to kWh / Gross Floor Area (m2)

ECI (AED/m2/yr) = Σ annual energy cost incl. DC capacity & consumption charges, fuel surcharge, VAT-exclusive / GFA

Blended rate (AED/kWh) = Total electricity cost / Total kWh

Cooling intensity (TRh/m2/yr) = Annual TRh / Conditioned floor area

Define the area basis once and use it everywhere: Gross Floor Area (GFA) per the building permit/affection plan, excluding open car parks. State whether enclosed car parks are included. Mixing GFA and Net Lettable Area is the most common benchmarking error.

## 2.5 Conversion factors

### District cooling to equivalent electricity

1 TR (refrigeration ton) = 3.517 kW thermal;  1 TRh = 3.517 kWh thermal = 12,000 Btu

Equivalent electricity (kWh_e) = TRh x DC system efficiency (kW_e/TR)

| Factor (kWh_e/TRh) | Represents | When to use |
| --- | --- | --- |
| 0.92 | Typical efficient UAE district cooling plant incl. auxiliaries (as specified in your brief) | Campaign default for portfolio comparison, unless the provider publishes a plant-specific value |
| 0.85 to 1.00 | Range of plant-level efficiencies reported by UAE DC operators | Sensitivity analysis |
| 1.0 to 1.4 | Typical in-building air-cooled/water-cooled chiller plant | Comparison for buildings with own chillers |
| 3.517 (thermal) | Site thermal energy, no plant efficiency | Only when a scheme asks for delivered thermal energy |

Confirm the factor required by the specific programme (e.g. Dubai Supreme Council of Energy/Taqati, Estidama, LEED, Al Sa'fat) before issuing reports. Always report raw TRh as well as converted kWh so the result can be recomputed.

Worked example: a 25,000 m2 office uses 4,200,000 kWh from DEWA and 3,500,000 TRh from Empower. Equivalent electricity for cooling = 3,500,000 x 0.92 = 3,220,000 kWh_e. Total = 7,420,000 kWh. EUI = 7,420,000 / 25,000 = 296.8 kWh/m2/yr.

### Fuel conversions (use supplier GCV where available)

| Fuel | Unit | Energy (kWh) | Emission factor (kgCO2e/kWh) |
| --- | --- | --- | --- |
| Natural gas (piped) | 1 m3 (standard) | ~10.5 (GCV ~38 MJ/m3) | ~0.184 (DEFRA/IPCC basis) |
| Natural gas | 1 MMBtu | 293.1 | ~0.184 |
| LPG | 1 kg | ~13.7 (GCV ~49.3 MJ/kg) | ~0.214 |
| LPG | 1 litre | ~7.1 | ~0.214 |
| Diesel/gas oil | 1 litre | ~10.6 (GCV ~38.1 MJ/L) | ~0.256 |
| Grid electricity, Dubai | 1 kWh | 1 | ~0.40 (use latest DEWA published factor) |
| Grid electricity, Sharjah/Ajman | 1 kWh | 1 | ~0.40 to 0.45 (use EWEC/MOEI or IEA national factor) |
| District cooling | 1 TRh | 0.92 kWh_e | 0.92 x grid factor |

Grid emission factors change yearly as solar (e.g. Mohammed bin Rashid Al Maktoum Solar Park) and nuclear (Barakah) capacity grows. Pull the latest published factor at the start of the campaign and freeze it in the project assumptions register.

## 2.6 Tariff handling

- DEWA commercial electricity uses slab tariffs plus a fuel surcharge per kWh; model savings at the marginal slab rate, not the average.

- SEWA and Etihad WE commercial tariffs differ; load the current tariff schedule from each utility website into the cost model on day 1.

- District cooling bills have a fixed capacity charge (AED/TR/yr) and a variable consumption charge (AED/TRh). EEMs reduce only the variable part unless the contracted capacity is renegotiated; state this explicitly in payback calculations.

- Report costs VAT-exclusive and state the tariff date.

# 3. ASHRAE Standard 211 Level 2 Report Structure

ASHRAE 211 (Standard for Commercial Building Energy Audits) defines minimum content for Level 1, 2 and 3 audits and includes normative report templates. A Level 2 audit builds on Level 1 with a detailed site survey, end-use breakdown, and EEM analysis with savings and cost estimates. The outline below meets the Level 2 requirements; check clause numbers against the edition your contract cites (2018 with addenda).

## 3.1 Table of contents

| Section | Content | Std 211 requirement |
| --- | --- | --- |
| Cover & document control | Building name, address, Makani/plot no., auditor, qualification, date, revision | Auditor identity and qualifications |
| 1. Executive Summary | Key metrics, benchmark rating, EEM summary table, total savings, cost, payback, CO2 | Required |
| 2. Facility Description | Use, GFA, age, occupancy, schedules, envelope, systems | Required |
| 3. Utility & Baseline Analysis | 12 to 36 months data, EUI, ECI, rates, weather normalisation, benchmark | Minimum 12 months, preferably 36 |
| 4. End-Use Breakdown | Calibrated model, reconciliation table, pie chart | Required at Level 2 |
| 5. System Assessment | HVAC, lighting, plug loads, DHW, envelope, controls/BMS, water | Required |
| 6. O&M Recommendations | No/low cost operational measures | Required |
| 7. Energy Efficiency Measures | Each EEM: description, savings, cost, financials, interactive effects | Required at Level 2 |
| 8. Implementation Plan & M&V | Packaging, phasing, M&V option (IPMVP) | Recommended |
| 9. Measures Considered but Rejected | With reasons | Required |
| Appendices | Bills, measurement logs, photos, calcs, equipment schedules, calibration certificates | Supporting data |

## 3.2 Section requirements

### Executive Summary (2 to 3 pages)

- Building snapshot: type, GFA, location, year built, operating hours.

- Baseline: annual kWh (electric + converted DC + fuels), cost (AED), EUI, ECI, CO2 (tCO2e).

- Benchmark position vs. UAE peer group (Section 4).

- EEM summary table: measure, savings kWh, savings AED, cost AED, simple payback, NPV, tCO2e.

- Total package savings as % of baseline; quick wins highlighted.

- Recommended next steps (Level 3 candidates, retrofit via ESCO under Dubai Etihad ESCO programme where relevant).

### Facility Description

- Space-type breakdown (m2), occupancy density, schedules (weekday, Friday/weekend, Ramadan).

- Envelope: wall/roof U-values (from drawings or estimated), glazing SHGC, window-to-wall ratio.

- Cooling source (DC, own chillers, DX), capacity, age, refrigerant.

- Air side: AHUs, FAHUs, heat recovery wheels, FCUs, VAV.

- Lighting inventory, controls, LPD (W/m2).

- BMS: scope, trending capability, set points observed.

- Equipment schedules in appendix.

### Utility & Baseline Analysis

- Monthly table and chart for each meter (kWh, TRh, gas), demand (kW), cost.

- EUI (kWh/m2/yr) and ECI (AED/m2/yr) with area basis stated.

- Regression vs. CDD with R2 and CV(RMSE).

- Blended and marginal rates per utility.

- Benchmark comparison and percentile.

### O&M Recommendations

Typical UAE no/low-cost items: raise space set points to 24 C, reset CHW supply temperature, fix BMS schedules running 24/7, close fresh air dampers in unoccupied hours, clean condenser coils, repair CHW insulation, enable VFDs left on bypass, recalibrate sensors, lighting timers for car parks and façades.

### Energy Efficiency Measures

Each EEM sheet must include: baseline condition, proposed measure, calculation method, energy savings (kWh, TRh, fuel), demand savings, cost savings (AED), implementation cost (+/-20% to 30% accuracy at Level 2), maintenance impact, simple payback, NPV, IRR/ROI, CO2 reduction, interactions with other EEMs, and risks.

Simple Payback (yr) = Implementation cost / Annual net savings

ROI (%) = (Annual net savings x Life - Cost) / Cost x 100     (or annual ROI = Savings / Cost x 100)

NPV = -C0 + Σ[t=1..n] (S_t - OM_t) / (1 + r)^t       S_t escalated at tariff escalation rate

CO2 reduction (tCO2e/yr) = Σ(ΔkWh_fuel x EF_fuel) / 1000

Suggested defaults (state in assumptions): discount rate 6 to 8%, tariff escalation 0 to 2%/yr, analysis period = measure life (LED 10 to 15 yr, VFD 15 yr, chiller 20 to 25 yr, BMS 10 to 15 yr).

### Interactive effects

Apply measures in sequence (lighting and plug loads first, then envelope, then HVAC) so that cooling savings from reduced internal gains are not double counted. In UAE climate, 1 kWh of lighting saved typically removes 0.25 to 0.35 kWh of chiller electricity.

### Typical UAE EEM library

| EEM | Typical savings | Typical payback |
| --- | --- | --- |
| LED retrofit + occupancy/daylight controls | 40 to 60% of lighting | 1.5 to 3 yr |
| Set-point and schedule optimisation (BMS) | 5 to 15% of HVAC | <1 yr |
| VFDs on AHUs, pumps, cooling towers | 20 to 40% of motor kWh | 2 to 4 yr |
| Chiller plant optimisation / replacement | 15 to 35% of plant kWh | 3 to 8 yr |
| CHW delta T recovery (DC buildings) | Reduces low-delta-T penalties, 5 to 10% TRh | 1 to 3 yr |
| Heat recovery on fresh air | 10 to 25% of FAHU cooling load | 3 to 6 yr |
| Demand-controlled ventilation (CO2) | 5 to 15% of cooling | 2 to 4 yr |
| Solar control film / glazing | 3 to 8% of cooling | 4 to 10 yr |
| Rooftop solar PV (Shams Dubai net metering) | Site-specific | 5 to 8 yr |

# 4. UAE EUI Benchmarking

## 4.1 Free local resources

| Resource | Owner | Use |
| --- | --- | --- |
| Building Efficiency Accelerator (BEA) Dubai and benchmarking reports | Emirates Green Building Council with WRI/UN | Published EUI ranges and retrofit guidance for Dubai building types |
| EmiratesGBC Technical Guidelines for Retrofitting Existing Buildings | EmiratesGBC | EEM guidance, benchmarking context |
| Dubai Building Energy Rating / Taqati and Dubai Supreme Council of Energy (DSCE) programmes | DSCE / Taqati / Etihad ESCO | Rating bands, retrofit programme, ESCO accreditation |
| DEWA Sustainability Reports and grid emission factor | DEWA | Carbon factor, consumption statistics |
| Al Sa'fat Dubai Green Building System | Dubai Municipality | New-build requirements, useful for EEM specs |
| Estidama Pearl Rating, Abu Dhabi DoE energy benchmarks | DMT / DoE Abu Dhabi | Cross-reference benchmarks |
| RSB Dubai District Cooling regulations | Regulatory & Supervisory Bureau | DC tariff and metering rules |
| ENERGY STAR Portfolio Manager | US EPA | Can be used for internal comparison only, not a UAE rating |
| Meteostat / degreedays.net | Open data | CDD for weather normalisation |

Rating band thresholds and programme names in Dubai have changed several times. Download the current version of each document at mobilisation and cite the version date in every report.

## 4.2 Indicative EUI reference table (kWh/m2/yr, total site energy incl. DC converted at 0.92 kWh/TRh)

| Building type | High efficiency | Median | Poor performing | Main drivers |
| --- | --- | --- | --- | --- |
| Commercial office | < 160 | 200 to 260 | > 320 | Cooling, lighting, 24/7 tenant loads |
| City hotel (3 to 5 star) | < 250 | 300 to 400 | > 480 | Cooling, DHW, kitchens, laundry, 24/7 operation |
| Resort hotel | < 300 | 350 to 500 | > 600 | Large low-density footprint, pools, F&B, landscape |
| Private school | < 110 | 140 to 200 | > 250 | Cooling, short operating hours, summer shutdown |
| Shopping mall | < 300 | 350 to 500 | > 600 | Long hours, high internal gains, food courts, atria |
| Residential tower | < 140 | 170 to 240 | > 300 | Cooling, common areas, pumps, car park ventilation |
| Healthcare clinic (reference) | < 250 | 300 to 400 | > 500 | Long hours, equipment, ventilation |

These ranges are indicative, compiled from published UAE benchmarking studies and typical audit results; they are not a regulatory rating. Replace them with your own campaign distribution after the first 50 buildings: report each building's percentile within the 200-building sample, which is a stronger benchmark than any external table.

## 4.3 Benchmarking procedure

- Use weather-normalised annual EUI (normal year CDD).

- Classify by primary use (>=75% of GFA); split mixed-use buildings by sub-metered area where possible.

- State inclusion/exclusion of car parks, retail podiums, data centres.

- Report percentile within campaign peer group and position vs. table 4.2.

- Flag buildings above the "poor" threshold as Level 3 candidates.

# 5. Equipment Rental Strategy & Local Supplier Logistics

## 5.1 Contract structure

- Master rental agreement with one primary supplier for Tier B kit (60-day term with a 2-week extension option), plus a secondary supplier as backup.

- Weekly rate negotiation: for 8+ weeks, ask for monthly rate pricing; typical discount vs. daily rate is substantial.

- Calibration clause: each instrument delivered with a valid ISO/IEC 17025 calibration certificate issued by an EIAC-accredited lab (or ILAC-MRA signatory), issue date within 6 to 12 months, certificate covering the ranges used in the field.

- Swap-out SLA: replacement within 24 to 48 hours for faulty units; spare unit held on site for power analysers.

- Damage/loss waiver: insurance clause and logger-loss pricing agreed in advance.

- Accessories list in the contract (CT sets, transducers, couplant, leads, cases, software licences).

- Training half-day hands-on session at delivery.

## 5.2 Calibration management

- Register every instrument (asset tag, serial, cert number, expiry) in the kit log.

- Verify each certificate on the EIAC directory (eiac.gov.ae) and check the scope covers the parameter.

- Do mid-campaign field checks (day 30): clamp meters against a reference source, lux meters cross-compared, thermo-hygrometers against a reference.

- Owned instruments: buy with factory or EIAC-lab certificates; plan recalibration at 12 months.

- Attach the certificate list as a report appendix (ASHRAE 211 traceability).

## 5.3 Supplier and calibration lab directory

The names below come from your brief and market knowledge. Scopes, addresses and accreditation status change; confirm each company's current EIAC scope, rental fleet and contact details directly before contracting. Do not rely on this table as verified accreditation evidence.

| Emirate | Company | Type | Typical operational scope (to verify) |
| --- | --- | --- | --- |
| Dubai | Alphatech | Instrument supplier/distributor | Test & measurement instruments, power and thermal equipment, sales/rental |
| Dubai | ACUME | Instrument supplier | Electrical and environmental test instruments, sales |
| Dubai | MeasureMart | Online/retail instrument supplier | Handheld meters for purchase: clamp, lux, anemometers, laser meters |
| Dubai | Totalcal | Calibration laboratory | Electrical, temperature, pressure, dimensional calibration |
| Dubai | Arabcal | Calibration laboratory | Multi-discipline calibration, on-site services |
| Sharjah | General Tech Services | Supplier/services | Testing instruments and calibration services |
| Sharjah | Al Khowahir | Supplier/calibration | Measurement equipment and calibration |
| Ajman | Perfect Calibration | Calibration laboratory | Electrical, mechanical, thermal calibration |
| Ajman | Core 4 Solutions | Supplier/services | Instrumentation and technical services |
| Regional | Brand distributors (Fluke, Testo, Hioki, Flir, Kimo, Chauvin Arnoux, Flexim) | Authorised distributors | Factory-calibrated new units, warranty, specialist rentals |

## 5.4 Logistics plan

| Item | Action |
| --- | --- |
| Kit hub | One central store (e.g. Al Quoz or Sharjah industrial area) to cut daily travel; teams collect Tier B kit by booking |
| Routing | Cluster buildings by area per day (Dubai south/north, Sharjah, Ajman) to keep 4 to 5 sites/day realistic |
| Kit calendar | Shared booking sheet for Tier B and loggers with deploy/retrieve dates |
| Data upload | Same-day upload to shared drive, naming convention BLDGID_DATE_INSTRUMENT |
| Heat | Summer roof and plant work before 11:00; store electronics out of vehicles (cabin temperatures exceed instrument storage limits) |
| Access | Gate passes and permits arranged 48 h in advance; FM escort required |
| Returns | Return check against delivery note, photos of condition, retain copy of certificates |

# 6. Quality Assurance Checklists

## 6.1 Field close-out checklist

- All MDB/SMDB readings taken and photos labelled.

- Loggers installed, positions recorded, retrieval date booked.

- Plant nameplates photographed.

- Set points and schedules recorded from BMS.

- FM interview form complete.

- Floor areas confirmed against drawings.

## 6.2 Report QA checklist

- 12 to 36 months of bills present, gaps explained.

- Area basis stated, EUI/ECI correct.

- Annual calibration error within +/-10% (target 5%).

- DC conversion factor stated and raw TRh reported.

- Every EEM has savings, cost, payback, NPV, CO2 and interaction logic.

- Tariffs and emission factors dated.

- Calibration certificates appended.

- Auditor qualification stated (e.g. CEM, CMVP, ASHRAE BEAP).

# Appendix A. References

- ANSI/ASHRAE/ACCA Standard 211, Standard for Commercial Building Energy Audits.

- ASHRAE Guideline 14, Measurement of Energy, Demand, and Water Savings.

- IPMVP Core Concepts, Efficiency Valuation Organization.

- ASHRAE Procedures for Commercial Building Energy Audits.

- EmiratesGBC Building Efficiency Accelerator and benchmarking publications.

- DEWA, SEWA, Etihad WE tariff schedules and sustainability reports.

- RSB Dubai district cooling regulatory framework.

- ISO/IEC 17025:2017 and EIAC accreditation directory.